ACCRÉDITATION SANS FRONTIÈRES · ISO 9001 READY

Life Safety Code Compliance (Hospital-Scale Fire Safety)

Standard Operating Procedure

Approved by Director, [ORGANIZATION NAME] [DIRECTOR NAME] ______________________ Date: __________

| Document Code | H-LSC-01-EN |
| --- | --- |
| Title | Life Safety Code Compliance (Hospital-Scale Fire Safety) |
| Edition | 1st Edition |
| Copy # | ___ |
| Effective Date | [EFFECTIVE DATE] |
| Next Review Date | [NEXT REVIEW DATE] |
| Organization | [ORGANIZATION NAME], Georgia |

# Table of Contents

1. Purpose · 2. Scope · 3. Definitions · 4. Real Generator/ATS Testing Requirements · 5. Interim Life Safety Measures (ILSM) · 6. Smoke Compartmentation · 7. Distribution of Responsibilities · 8. Accompanying Documentation · 9. Approval Sheet · References

# 1. Purpose

To ensure [ORGANIZATION NAME] meets the real, hospital-scale fire and life safety requirements of NFPA 101 and NFPA 99 — genuinely more complex than the general facility fire safety already covered in H-CC-08, since a hospital cannot simply evacuate patients the way an ambulatory clinic can [1–4].

# 2. Scope

Applies to the entire physical plant of [ORGANIZATION NAME]'s hospital facility. This document expands, rather than replaces, H-CC-08's general fire safety principles.

# 3. Definitions

•  Defend in place — a real, hospital-specific fire strategy distinct from full evacuation, since moving critically ill or immobile inpatients is itself a real risk [1]

•  ILSM — Interim Life Safety Measures, required under real standard EC.02.06.05 whenever construction, renovation, or demolition compromises life safety features [4]

# 4. Real Generator/ATS Testing Requirements

[ORGANIZATION NAME]'s emergency generators and automatic transfer switches (ATS) undergo real, specific testing — not the general backup-power testing in H-CC-12 alone: monthly operational testing of ATS, full load testing under load for a minimum of 30 minutes monthly, and an annual 4-hour load bank test [4]. All test records demonstrate the system transferred within the required 10-second window for life safety and critical branches — a real, specific, measured number, not “quickly” [4].

# 5. Interim Life Safety Measures (ILSM)

Whenever construction, renovation, or demolition activities compromise [ORGANIZATION NAME]'s life safety features, real ILSM protocols activate — additional fire watches, temporary alarm/detection compensating measures, and staff notification, not simply proceeding with reduced protection until construction ends [4].

# 6. Smoke Compartmentation

[ORGANIZATION NAME]'s hospital building maintains real smoke compartmentation enabling horizontal patient movement to a protected zone on the same floor — the real basis for defend-in-place, distinct from H-CC-08's general facility fire response [1].

# 7. Distribution of Responsibilities

| Task | Director | Facility/Maintenance Lead | - | - |
| --- | --- | --- | --- | --- |
| Approval of this SOP | Final |  |  |
| Generator/ATS testing schedule |  | Responsible |  |
| ILSM activation during construction |  | Responsible |  |

# 8. Accompanying Documentation

| Code | Title |
| --- | --- |
| H-LSC-01-F01 | Generator/ATS Test Record |
| H-LSC-01-F02 | ILSM Activation Checklist |
| H-CC-08 | General Facility & Fire Safety |
| H-CC-12 | Electrical Safety & Backup Power |

# 9. Approval Sheet

| Role | Date | Signature |
| --- | --- | --- |
| Prepared by: [FACILITY/MAINTENANCE LEAD NAME] | ___________ | ___________ |
| Agreed by: [DIRECTOR NAME] | ___________ | ___________ |

References

[1] NFPA 101. Life Safety Code — smoke compartmentation, defend-in-place basis.

[2] Consulting-Specifying Engineer. NFPA 99: A Fire and Life Safety Perspective — defend-in-place concept, smoke zone alignment.

[3] ANSI Blog. NFPA 99, Health Care Facilities Code — NFPA 99 vs. NFPA 101 scope distinction.

[4] iFactory. NFPA 99 & Life Safety Code for Healthcare — real generator/ATS testing intervals, 10-second transfer window, EC.02.06.05 ILSM standard.